Date: 19/09/2014

Incident Report

Sub. : Incident report of failure of Train-C Granulator motor (6.6kV 350Kw) on 11.09.2014

1.0 	Details of the event

Incident reported-

Granulator motor was running normal ( in forward direction running) with normal plant load. TRAIN-C was stopped at around 09.30 hrs for routine maintenance. After stoppage of the plant, its granulator motor is required to run in reverse direction running mode as per process requirement. Complaint was received from control room that Granulator was not taking start in reverse mode.

Action taken-

Shift –in-charge along with technician immediately went to the 6.6 KV switchgear panel (at SS-3 having its feeder)  and observed no problem on the feeder panel . So clearance given for starting , it instantly tripped but relay did not show any fault.

Following actions were taken –

- Breaker was taken in to test mode to check the breaker start & stop from LCS/DCS. Initially  breaker was found tripping from DCS stop at test mode. After checking from panel,  DCS start & stop was found O.K.

- I.R. value of the motor taken from (behind) the panel side with 2.5 KV megger , it’s value was 1.5 G-ohm ( Ph-E).

- To rule out the possible defect in motor protection relay, they have been swapped between its forward and reverse starter panels.

Again, the clearance given for starting in reverse mode but the motor tripped on instantaneous unbalance current fault.

Around 11.30 hrs it was decided to check the motor terminals. Following were the

observations /actions-

- Motor body was found clean and body temperature found normal.

- Motor power and star point terminals open.

- Both side terminals were found clean & terminal tightness was also found proper. No  sign or smell of heating observed .

- IR value of each winding taken ( after opening the star point ) – found 1.5 G-ohm ( Ph-E) each winding , ph-ph >5 G-ohm.

- Resistances and inductances also checked for all the three windings and found balance.

- The breakers were swapped between forward and reverse panel to rule out the possibility of any unbalance due to time difference of closing of the pole.

Clearance given for starting in reverse mode but it tripped  without showing any display

on the relay. So all the CT connections /tightness checked  and   clearance   given for

starting but the motor tripped on unbalance current. It was   observed   that the   relay   was  showing erratic reading and also one hot spot observed inside the relay cabinet.

So it was decided  to   replace the relay   with   chassis. The relay was replaced by

spare relay.

As there was problem with the panel (reverse mode), it was decided to check the

motor to start at decoupled condition in forward mode.

After decoupling the motor started in forward mode, the motor run for about 30

Seconds and tripped on unbalance current.

Then surge arrestor were removed from  both the  forward and reverse panel and IR value taken again from the behind of the panel ( forward ) with 2.5 KV Meggar and the value was found 250 M-OHM (Ph-E).

Then the  motor started in forward mode ( without suppressor ), the motor

tripped on unbalance current and Earth fault.

Then immediately the motor terminals and star point terminals open and checked for IR value and resistance and inductances of the windings.

IR value of R-phase found : 110 m-ohm, Y-phase :1.5 G-ohm, B-phase : 1.5 G-ohm

Resistances and inductances of R-  phase found  : Open

Resistances and inductances of Y &  B  phase found O.K.

Immediately the motor offered for replacement.

2.0 	Break up of time

Details of breakdown of Granulator motor are  as under:

1 ) Checking of motor in reverse mode

From 10.00 hrs to  : 14.00 hrs

2) Checking of motor in forward mode ( decouple condition )

From 14.00 hrs to  : 17.00 hrs

3 ) Motor given for replacement  at 17.30 hrs.

4 )Clearance received for connection and trial : at 05.40 am on 12.09.2014

5 )Replaced motor hand over for coupling : at 07.00 am 12.09.2014

3.0 	Probable cause of failure

Preliminary cause seems failure  of the insulation of the winding due to aging effect. The fault did not develop immediately but took time i.e. after few starts & few seconds run, one phase winding became open.

4.0 	Recommendation

Motor shall be tested for monitoring its health i.e. dielectric losses trends ( tan delta test) shall be maintained.