INDEX

| SR.NO. | TOPIC | PAGE NO. |
| --- | --- | --- |
| 1 | ECONOMISER | 4-11 |
| 1.1 | ECONOMISER COIL REPLACEMENT | 4-11 |
| 1.2 | ECONOMISER CASING REPLACEMENT & INSULATION WORK | 11 |
| 2 | CONVECTION BANK | 12-17 |
| 2.1 | CONVECTION BANK TUBE REPLACEMENT | 12-15 |
| 2.2 | REFRACTORY WORK AT CONVECTION BANK | 16-17 |
| 3 | EVAPORATOR COIL | 18-22 |
| 3.1 | EVAPORATOR COIL REPLACEMENT | 18-21 |
| 3.2 | REFRACTORY & INSULATION WORK AT EVAPORATOR COIL | 22 |
| 4 | IBSH COIL | 23-24 |
| 4.1 | IBSH COIL REPLACEMENT | 23-24 |
| 4.2 | REFRACTORY WORK AT IBSH COIL | 24 |
| 5 | IBSH I/L HEADER ALLIGNMENT | 25-26 |
| 6 | RLA STUDY | 27-32 |
| 7 | BUNKER JOB | 32 |
| 8 | MUDDRUM REPAIR WORK | 33-36 |
| 9 | EXTRA MODIFICATION FOR BOILER HEALTHINESS | 37-43 |
| 9.1 | FURNACE | 37-39 |
| 9.1.1 | REFRACTORY APPLICATION AT BED PLATE OF FURNACE | 37 |
| 9.1.2 | REFRACTORY APPLICATION AT EVAPORATOR COIL | 37-38 |
| 9.1.3 | EXTRA HINGE SUPPORT PROVIDED AT IBSH COIL | 38 |
| 9.1.4 | EXTRA ASH DRAINS PROVIDED IN BED PLATE | 38-39 |
| 9.2 | ECONOMISER | 39-40 |
| 9.2.1 | SS TUBE ARRANGEMENT PROVIDED AT TOP ZONE | 39 |
| 9.2.2 | SS BOX ARRANGEMENT PROVIDED AT U BENDS | 40 |
| 9.3 | SPRING SUPPORT PROVIDED AT ATTEMPERATOR HEADER | 41-43 |
| 10 | MISC JOBS | 44-54 |
| 10.1 | DCF MAINTENANCE | 44 |
| 10.2 | REPLACEMENT OF COAL NOZZLE ASSEMBLY | 44 |
| 10.3 | ESP MAINTENANCE | 44-45 |
| 10.4 | FAN MAINTENANCE | 45-47 |
| 10.5 | DAMPER REPLACEMENT/MAINTENANCE | 48-49 |
| 10.6 | APH TUBE MAINTENANCE | 49-50 |
| 10.7 | PA LINE MAINTENANCE | 50 |
| 10.8 | FURNCE CLEANING,PINNING & BED MATERIAL CHARGING | 50-51 |
| 10.9 | PAINTING WORKS IN BOILER-2 | 51-52 |
| 10.10 | DIESEL BURNER REPLACEMENT | 52 |
| 10.11 | Valve replacement | 53 |
| 10.12 | FLOWMETER ARRANGEMENT AT CBD LINE | 53 |
| 10.13 | HYDROTEST | 53 |
| 11 | COMMISSIONING OF BOILER | 54-60 |
| 11.1 | REFRACTORY DRY OUT | 54-57 |
| 11.2 | ALKALI BOIL OUT | 54-57 |
| 11.3 | STEAM BLOW-OUT | 58-60 |
| 12 | BOILER LIT-UP & STEAM CHARGING | 60 |
| 13 | ANNEXURES | 61-64 |
| 13.1 | ANNEXURE FOR ACTUAL SHUTDOWN COSTING | 61-62 |
| 13.2 | ANNEXURE OF TIME CHART FOR SHUTDOWN ACTIVITIES | 63-64 |

1.0 ECONOMISER

1.1 ECONOMISER COIL REPLACEMENT

Problem

Economiser coil found eroded and leaked several times ,economizer coils are divided in three zones(top zone,middle zone & bottom zone).Complete economizer coil has been replaced for boiler reliability.

Execution of job

Job has been executed by M/S Unique construction & Engg.Many skilled and semi skilled labour involved for execution of job.W.O No.-6540/252004141801.

Sequential steps:

1. Shut down the boiler by normal shut down procedure.

2. Allow to cool the boiler naturally.

3. Remove Economizer casing insulation.

4. Make proper lifting arrangement to remove old eco coil from modules.

Follow the activities as per activity no mention in respective drawings. Same is describe below:

1. Remove economizer casing from boiler LHS(ref.drg.)

2.Cut weld joint to free eco coils for Ist module. Care should be taken to maintain stub length min 160mm(refer dwg.) while tube cutting from header/ bend.

3. After eco coil weld joint cutting as indicated in above dwg. Ladder supports to be remove on by one. Each ladder support free 2 eco coil.

After removal of free coil from module further ladder support to be remove and same procedure repeat till all module 1st coil removing get done.

4. After module Ist coil removing remove all anti channeling plates except top and bottom as mention in dwg. Same has to be done after removing of IInd module coils.

5.After complete removal of eco Ist module. Cut eco coil weld joint for II nd module as mention in following dwg. Maintain 160 mm min stub length. Repeat all step same as required for module Ist.

6. For placing new eco coil follow all sequence for removal in reverse.

PHOTOGRAPHS

Old casing removed of all three zone in economizer

Old economizer coil dismantling work

Economizer coil erection completed in all three zones

INSPECTION REPORTS

Radiography inspection report of economizer coil as per IBR requirements

Radiography inspection report of economizer coil as per IBR requirements

1.2 ECONOMISER CASING REPLACEMENT

Economiser casing replaced in bolted types in different panels instead of previously welded type casing.This bolted type casing is useful for easy inspection of economizer without cutting & welding of casing.

2.CONVECTION BANK

2.1Convection tube replacement

Complete set of convection bank tubes has been replaced (total quantity-740 nos)

Problem

25 nos of bank tubes have been plugged and remaining tubes thickness found less. These tubes may be leaked in future and cause of boiler shutdown (production loss)

Sequential Step:-

1. Water Drum to be locked as per attached drawing.

2. Steam drum and Water drum manhole to be opened.

3. Remove the Convection bank casing from Boiler RHS and LHS.

4. Remove the ash from convection bank.

5. Dismantling of drum internals to be done from Steam Drum side, marking should be done in drum Internals for identification purpose.

6. Steam and Water drum cleaning and drying to be done. _

7. Remove the Boiler bank tube as per below procedure

Procedure

a. Cut the tube at both ends of the tube leaving 10mm from the drums shell outer surface.

b. Cut the tube in to small quadrant of the bell-mouthed portion of the tube inside the drum.

c. Heat the tube ends by gas torch up to 600°C / 650°C (max.). Care should be taken that no damage or unnecessary heating happens to drum shell.

d. While the tube end is hot, fold the tube ends to inside by a suitable screwdriver/square bar and a small hammer. Screw driver/square bar end to be round off to avoid any 
damage to tube sheet holes. In this process a small gap will be created between drum holes and tube end.

e. This procedure shall be followed for Steam Drum from inside and for Water Drum from outside.

f. On completion of step 3 & 4, 50 % of the tube end circumference to be heated by gas torch from inside the tube. Push the tube toward the center with the help of screwdriver through gap between drum holes and tube by light hammering on the screwdriver.

g. Hold the screwdriver end slightly little inclined towards the tube ends, so that no scratch mark /damage on the drum holes.

h. Repeat this process till the screwdriver penetratestill the end of the drum holes. After this a gap will be formed between tube end and drum holes.

i. On completion of 6, the tube end to be gas cut exactly near the gap formed.

j. On completion of 7, one end of the tube to be collapsed by pushing screwdriver inside the gap between outside the tubes and drum holes.

l. On completion of tube removal, drum hole shall be thoroughly inspected.

8. After removing of convection tubes drum hole cleaning to be done.

9. Convection tube alignment to be done as per convection bank assembly drawing 
	and tube expansion to be done as per below attached procedure.

Bank Tube Expansion Guidelines

Purpose

The purpose of this work instruction is to outline the procedure to be followed while expanding the boiler bank tubes.

Cleaning

Tube ends inside and outside shall be cleaned with abrasive paper, wire brush, buffing wheels or solvents untill the metal is free from paint, oil, grease or any other foreign materials. Sufficient length of the tube end shall be cleaned to ensure that foreign matter does not get into the tube sheet during tube insertion and expansion.

Drum holes shall be cleaned with abrasive paper & solvent untill the metal is free from paint, oil, grease or any other foreign materials. Care must be taken to dry the metal as the lequid trapped between the tube and tube sheet prevents the metal to metal binding.

Expander selection

Propulsive type three roller expanders shall be used. For drum plate thickness upto 43 mm, the tube end shall be expanded the full depth of the seat plus the tube projection in the drum and a minimum of 3 mm to a maximum of 10 mm beyond the seat (outside the drum).

For drum plate thickness over 43 mm, the length of the expanded tube end shall be limited to 43 mm plus the tube projection inside the seat. However, the effective roller length shall not exceed 63 mm.

Seperate expanders shall be used for parallel and bell mouth expansion.

Drives for tube expanders

There are mainly two types of drives for tube expanders other than manual ratchets viz. Pneumatic and electrical drive.

Both the drives uses the torque control unit. This provides uniform tube expansion by accurate control of torque. The control unit automatically controls the tube expanding with uniform/ repeatable accuracy.

The torque setting required for tube expansion can be determined by mock up test on the job. Start at a lower setting of the torque and check inside diameter of the tube after expansion.

Repeat the operation till the correct dimension as per the formula given in this instructions is achieved.

The unit is now ready for complete use. This torque setting gives uniform tube expanding.

After expanding of each tube the expander rotates in oppositedirection which facilitates easy removal of expander.

M/s Power Master Engineers Pvt. Ltd., Bombay is the main supplier of expanders with both types of drives.

Expander inspection and care

Before use on the job and during the use, the expander rollers and mandrel shall be checked for wear, scars and chipping. Defective rollers and mandrel shall not be used.

The expander shall be thoroughly washed in solvent / light oil to remove foreign matter before and during the use.

During the use oil lubricant shall be applied on the expander as well as tube end (inside) as required. The care shall be taken for oil not to panetrate between tube & tube sheet which may create improper binding between metal to metal.

Dimensional information and inspection for expanding tubes

The dimensions of tube ends and tube sheets shall be taken at random as follows :

1.Tube end wall thickness 	(5 to 10 tubes at random)

2.Tube end outside diameter 	(5 to 10 tubes at random)

3.Drum hole inside diameter 	(5 to 10 holes at random)

The measurements obtained as above shall be recorded and the calculations are made to determine the range of readings expected after final expanding.

The calculations shall be made based on following example to determine the final internal diameter of tube after expanding.

 Example shown below for a nominal tube size of 50.8 OD x 4.5 THK. With theoratical hole size of 51.60 mm.

For all practical purposes, average readings obtained shall be considered.

Example

Average drum hole diameter

Average tube outer diameter

Seat clearance

Average tube outer diameter

Less average tube thickness (2 x 4.5)

Tube internal diameter

Add seat clearance

Tube internal diameter at metal to metal contact

Expected increase of tube internal Diameter

(8% of tube thickness x 2)

Expanded tube internal diameter

51.60mm

50.80mm 
	0.80mm 
50.80mm 
09.00mm 
41.80mm 
	0.80mm 
42.60mm

0.72 mm 43.32mm

The amount of tube expansion shall range from 6 % to 14 % of tube thickness greater than the calculated tube internal diameter at metal to metal contact with the tube seat.

Go-No go gauges shall be used based on % thinning given as above for inspection purpose. The record shall be maintained in the stage inspection register for 100 % tubes.

Bank Tubes Assembly and Expanding

After the drums are aligned in position, the insertion of bank tubes shall proceed in the following sequence.

Three rows (circumferential) of tubes, preferably one each on either side ofdrums & one in the 
center shall be inserted for final verification of drums alignment and the correctness of the supplied 
tubes.

Expand all three rows after setting the tube projection inside the drums as per Q.A. plan. Expanding sequence shall be from center to outwards. This will ensure the locking of drums. The projection of tube inside the drum should be maximum 12mm and minimum 6mm.

Insert two rows (center most rows along the length of drum) of tubes. Clamp and align the tube rows using wooden spacers.

Expand these rows after setting the tube projection inside the drums as per Q.A. Plan. Expanding sequence shall be from center towards drum ends. The expanding shall be first carried out in upper drum & than lower one.

Progressively insert, align & expand the alternate rows of tubes on either side of drum center line (along the length of the drums.) Follow the expanding sequence as above.

Tube ends shall be flared after completing 100% expansion and flaring shall be ensured as per drawing & Q.A. plan.

Go - No go gauges shall be used for inspection & record shall be maintained in stage inspection register.

PHOTOGRAPHS

Cnvection bank tube replacement work is under progress

Complete Convection bank tube replaced

2.2 Refractory work in Convection bank

(Tiles fitting)                                                                                     Hysil block fitting

Refractory work is under progress

3. EVAPORATOR COIL

3.1Evaporator coil replacement

Complete set of evaporator coil have been replaced (total 264 coil)

Problem

Evaporator coil found eroded at bottom side and may be leaked in future any time(production loss)

Due to this management decided to replace complete set(264 nos)of evaporator coil for boiler reliability and healthiness.

Objective

Over a period of operation, the inbed evaporator coils in AFBC Boiler are vulnerable for erosion from furnace side, hence the inbed evaporator coil replacement forms an integral part of longterm predictive maintenance practice.

Apart from replacing entire coil assembly, at times part replacement may be undertaken due to unexpected failures.

The guidelines in this write-up have been prepared with the following objectives:

 For effective planning & execution of inbed coil replacement jobs.  Detail procedure for the replacement of inbed evaporator coils in full or in part.

Analysis :

Complete coil replacement is based on the follow ing parameters or in combination .

 Erosion pattern

 Erosion rate 
 Failure history

 Maintenance practices 
 Operation practices 
 Changes in fuel quality

To confirm the requirement of complete coil replacement, carry out extensive visual examination and ultrasonic thickness gauging of the complete inbed evaporator coils at regular intervals. Based on the thickness gauging data, decision can be arrived to go for either spool replacement or complete replacement of inbed evaporator coils.

Coil replacements are undertaken during planned annual shutdown and also during unplanned failure situations.

Prerequisites for Inbed Evaporator Coil replacement .

 Availability of spare inbed evaporator coils.

 Refractory for the inbed coils and repairs in combustor as required. 
 Ground inspection of each coil to check for any transit damage / dimensional deviations and rectification as required.

 Completion of all IBR formalities / permissions as required.

Last but not the least, skilled workers who plays a vital role in this job, hence it is always advisable to deploy a workforce with previous experience in this job.

Prior start the entire coil replacement follow ing activity to be carried out ;

 Drain the entire bed material from the combustor.

 Flush the pre boiler sections up to economiser Fill the boiler drum and flush the 
economiser by opening economiser bottom header drain.

 Flush the HP heater by opening feed water control valve bonnet.

 Flush the boiler drum and down comers, through down comer supply pipe connected for compartments separately.

 Inspect & clean the feed water distribution pipe inside the steam drum.

 Drain the boiler completely.

 Cut the evaporator coil bottom header end cap, inspect the header for accumulation of 
foreign particles if any. Clean the headers as required.

 Cut the front and rear header end caps.

Coil replacement :

Coil can be replaced either from outside the furnace or from inside the furnace depends on the maintenance requirement.

Hence the decision on adopting any of these method should be made after due consideration on previous experience and condition of combustor refractory.

Replacement form outside the furnace :

In this method, the coils are cut and re-welded from outside the furnace casing. Advantages of out side replacement method :

 Comparatively easier for cutting and edge preparation of the coils.

 Better weld position.

 Comparatively easy for coil alignment.

 Ease for radiography / repairs of weld defects if any.

 Weld joints can be easily inspected during hydro-test.  Ideal in cases of erosion on bed coils exist.

Disadvantages of out side replacement method :

 Requires stripping off and re-building entire bottom furnace refractory and casing, thus 
requires additional refractory material, manpower and work content.

 External immovable components / layout restrictions may cause space constraints. 
 Refractory curing and dry out required after work completion, thus increasing start up 
time.

Out side furnace Coil Replacement Procedure:

1.Mark the IBE coils detail, i.e. row nos. (i.e. LSH 1inner, 1outer . RSH 1inner, 1outer, etc.) with paint.

2.Mark the cutting line with marker as per the below sketch.

3.Cut the coils one by one with hacksaw/grinder (use cutting wheel to avoid excess metal loss) and remove them out of the furnace.

4.Make the edge preparation of the new coils and the coils with the header.

5.Flush the coils welded to header with water jet, first the top header then bottom header 
coils with pressure 5 to 6 kg/cm2

6.Inspect the headers with boroscope and clean the headers as required.

7.Clean all new coils with Potable water source with pressure 5 to 6Kg/cm2 and flush & dry the coil with air pressure 5 to 6Kg/cm2 and carry out ball pass test, once ball test is 
completed coil is ready to weld fit up.

8.While weld fit up ensure the coils alignment and the coil row nos. as marked prior to 
removal.

9.Complete the welding as per the weld procedure. (use appropriate filler metal & welding rod )

10.Conduct the NDT test as per the quality plan.

11.After the clearing the NDT, blank the open header end caps by suitable wooden plugs.

12.Fill the boiler up to the evaporator top header by DM/ Potable water and remove the 
wooden blank for flushing the header of one opening. Repeat the same no. off times for all the compartments/sections separately for both the sides.

13.Inspect the header and near by coils with fiber optic instrument and repeat the cleaning as per the requirement. Some heavy particles may still be there at bottom headers . These can 
be removed manually through the header end cap openings.

14.Re-weld the header end caps after ensuring header cleanliness.

15.Hydro test to be carried out.

Precaution :

 The coil should not be cut on the bend portion / very near to the bend. 
 Distance / reference should be taken from header and each coil should be marked 
individually.

3.2 Refractory & insulation work at evaporator bed coil

After completion of evaporator coil replacement refractory work done at evaporator coil

PHOTOGRAPHS

Refractory removal and evaporator coil replacement is under progress

Complete Evaporator coil replaced

INSPECTION REPORTS

R

Radiography inspection report of evaporator bed coil(as per 10% IBR requirement)

4. IBSH COIL

4.1 IBSH coil replacement

Problem

IBSH coil found sagged around 500 mm in upward direction from its original position due to this management decided to replace complete set of Inbed super heater coil.

Sequential steps:

1.Boiler stoppage.

2.Natural cooling to avoid any thermal shock to boiler.

3.At the end of natural cooling 70-80*c DM water circulation

4.Boiler draining before tube cutting .

5. Bed material to be drained just after boiler stoppage to reduce natural cooling time.

6. Furnace cleaning and FD air nozzle covering with GI sheet or felt (coal transmission belt used in coal plant).

8. Header locking.

9. Tube cutting

10. IBSH coil Alignment.

11. Tube welding.

12.All locking removal. 
13 Hydraulic Test.

PHOTOGRAPHS

IBSH coil (old position)                                                                    IBSH coil (after replacement)

IBSH coil replaced                                                             Refractory work completed in IBSH coil

INSPECTION REPORTS

Radiography inspection report of IBSH coil

5. IBSH INLET HEADER ALLIGNMENT

IBSH inlet header found dislocated in horizontal and vertical position

Vertical position-110 mm

Horizontal position-40mm(towards furnace side)

Above said dislocation has been rectified by required cutting Primary sup.heater O/L header.

40 mm

960mm

1070mm

Dislocated  position of IBSH inlet header                                         IBSH inlet header cutting for alignment

1000mmm

1000mmm

IBSH header welding after alignment                             Current position of IBSH I/L header(after alignment)

INSPECTION REPORTS

IBSH header radiography inspection and SR report

6. RLA STUDY

In RLA study Different kind of NDT and DT activities done, Discretion of these activities are given below

| Sr. No. | Area | Location |  |  | Test to be carried out |
| --- | --- | --- | --- | --- | --- |
| 1 | Steam Drum | - Internally and Externally - Drum ID checking & Thickness. - ‘L’/‘C’ seam, base metal and HAZ (Heat Affected Zone)On replica locations - 12” x12”spots on ‘L’ & ‘C’ seams & base metal. - Safety valve stubs & integral piping on dish ends, Stubwelds. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - In situ Metallography (Replication) - Hardness testing - Ultrasonic Flaw Detection (UFD) - DPI / MPI - Deposit Analysis |
| 2. | Water Drum | - Internally and Externally - Drum ID checking & Thk. - ‘L’/‘C’ seam, base metal and HAZ (Heat Affected Zone)On replica locations - 12” x12”spots on ‘L’ & ‘C’ seams & base metal. - Safety valve stubs & integral piping on dish ends, Stubwelds. - Drum Internal deposits, if any |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - In situ Metallography (Replication) - Hardness testing - Ultrasonic Flaw Detection (UFD) - DPI / MPI - Deposit Analysis |
| 3. | Economizer Coils | - Overall - From Inlet & Outlet tubes as accessible.(2 numbers) |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - Tube sample of 500 mm length for Laboratory Analysis. |
| 4. | Economizer Header | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 5. | In Bed Evaporator Tubes | - Overall - From Inlet & Outlet tubes as accessible.(2 numbers) |  |  | - Visual Inspection - Dimensional Measurement - Ultrasonic Thickness Gauging - Tube sample of 500 mm length for Laboratory Analysis. |
| 6. | In Bed Evaporator Headers | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 7. | Primary Superheater Tubes | - Overall. - From Inlet & Outlet tubes as accessible.(2 numbers) |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging. - NOTIS® - Tube sample of 500 mm length for Laboratory Analysis. |
| 8. | Primary Superheater Header | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 9. | In-Bed Superheater Tubes | - Overall. - From Inlet & Outlet tubes as accessible.(2 numbers) |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging. - NOTIS® - Tube sample of 500 mm length for Laboratory Analysis. |
| 10.0 | In-Bed Superheater Header | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 11 | Boiler Bank Tubes | - Overall. |  |  | - Visual Inspection - Dimensional Measurement - Ultrasonic Thickness Gauging. - RFET. |
| 12 | Furnace Water Wall Tubes | - Overall. - From Front, Rear & Side Wall tubes as accessible.(4 numbers) |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging. - FHyNESTM. - Tube sample of 500 mm length for Laboratory Analysis. |
| 13 | Furnace Wall Header | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 14 | Attemperator Header | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 15 | Main Steam Line | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 16 | Risers, Downcomer & all connecting Pipes | - Externally - OD checking. - Weld, HAZ & Base metal. - On replica locations - Weld, HAZ & Base metal. - Stub weld & Header weld joints. |  |  | - Visual Inspection. - Dimensional Measurement - Ultrasonic Thickness Gauging - In situ Metallography (Replication)Hardness testingUltrasonic Flaw Detection (UFD) - NDT (DPI / MPI) |
| 17 | Feed Water Piping. | - Inlet & Outlet header - Header OD & thickness checking. - Stubs weld joints. - Through cut stub joints or drains. - Weld, HAZ & Base Metal. |  |  | - Visual Inspection - Dimensional Measurement, - Ultrasonic Thickness Gauging - NDT (LPI / MPI) - Fiberoptic Test. - In-situ Metallography. - Hardness Testing. - Ultrasonic Flaw Detection (UFD). |
| 18 | APH |  | All tubes & the locations where the CA-RLA study needs to be carried out as per standard practice. | - RFET |  |

15 nos of header end caps cutting done for visual inspection (fibroscopy), Description of these headers end caps with UT & SR report of weld joints are given below.

| Sl.No | DESCRIPTION | MOC | UT status | SR completion status |
| --- | --- | --- | --- | --- |
| 1 | Economizer inlet header | SA 106 GR.B | Completed | Not required |
| 2 | Economizer outlet header | SA 106 GR.B | Completed | Not required |
| 3 | Inbed Evaporator TOP header (LHS) | SA 106 GR.B | Completed | Not required |
| 4 | Inbed Evaporator BOTTOM header(LHS) | SA 106 GR.B | Completed | Not required |
| 5 | Inbed Evaporator TOP header (RHS) | SA 106 GR.B | Completed | Not required |
| 6 | Inbed Evaporator BOTTOM header(RHS) | SA 106 GR.B | Completed | Not required |
| 7 | Primary superheater I/L header | SA 106 GR.B | Completed | Completed |
| 8 | Primary superheater O/L header | SA 335 GR.P11 | Completed | Completed |
| 9 | Inbed superheater I/L Header | SA 335 GR.P11 | Completed | Completed |
| 10 | Inbed superheater O/L Header | SA 335 GR.P11 | Completed | Completed |
| 11 | Furnace side wall top header(RHS) | SA 106 GR.B | Completed | Completed |
| 12 | Furnace side wall Bottom header(RHS) | SA 106 GR.B | Completed | Not required |
| 13 | Furnace side wall top header(LHS) | SA 106 GR.B | Completed | Completed |
| 14 | Furnace side wall Bottom header(LHS) | SA 106 GR.B | Completed | Not required |
| 15 | Attemperator Header | SA 335 GR.P11 | Completed | Completed |

PHOTOGRAPHS

RFTE of APH tubes                                                                               Header end caps cutting for inspection

Sample tube cutting from furnace panel                                        Sample tube cutting from PSH

Panel header end cap edge prepration                                         Different NDT in RLA job

INSPECTION REPORTS

Radiography inspection report of RLA job

7. BUNKER JOB

There are some sheeting job done at roof and side wall, new beam erected in coal bunker and damaged grating has been replaced.

PHOTOGRAPHS

Bunker before sheeting                                                             Bunker after sheeting

8. MUD DRUM REPAIR WORK

Mud drum found damaged at 8 places on outer shell area. It was inspected and proper repair welding done at effected zone.

Mud drum(before repair)                                                       Mud drum(after repair)

REPAIR PROCEDURE FROM M/S THERMAX

INSPECTION REPORTS

Radiography inspection report(before repair)         Radiography inspection report(after repair)

Post weld heat treatment report(SR report-after muddrum repair)

9. EXTRA MODIFICATION FOR BOILER HEALTHINESS

9.1 FURNACE

9.1.1 REFRACTORY APPLICATION AT BED PLATE OF FURNACE

Problem

Due to insufficient FD air pressure, when bed height of furnace reaches 400 mm(designed) the fluidization of bed material become poor and  it is the cause of low bed temp,low steam generation, high LOI and PA line choking.

It was suggested by M/S Thermax Ltd. to provide a 50 mm refractory layer on bed plate of furnace bubble cap length is 150 mm and air holes are at only top portion(25 mm) of bubble caps .If 50 mm bottom portion of bubble cap will merged in refractory than the path length of air flow will be less and it will improve the fluidization  and may useful for avoiding such type of aforesaid problems

Bed plate (before refractory application)                        Bed plate (after refractory application)

9.1.2 REFRACTORY APPLICATION AT EVAPORATOR COIL

Problem

Due to high erosion at coal nozzle area in furnace, our evaporator coil at said location found highly eroded and frequent failure occurs at these eroded location. To avoid leakage of coil, Our OEM M/S Thermax Ltd suggested to provide special erosion resistant refractory(PHOSCAST-90 XR) at bottom zone of evaporator coil in coal nozzle area.

Refractory application at evaporator coil in coal nozzle area

9.1.3 EXTRA HINGE SUPPORT PROVIDED AT IBSH COIL

Problem

There are two hinge support in In Bed Super Heater(IBSH) coil at furnace, It is Inadequate to support the IBSH coil properly. Due to this IBSH coil sagged 500 mm in upward direction at bend portion.

It was suggested by Thermax to provide an extra hinge support in IBSH coil to avoid sagging problem.

IBSH coil in sagged condition                                           Extra hinge support fitting at IBSH Coil

9.1.4 EXTRA BED ASH DRAIN LINE PROVIDED IN BED PLATE

Problem

There is one bed ash drain line in each bed of furnace. At the time of rainy season clinker formation occurred in furnace due to moist coal ,It is essential to drain out this clinker from the furnace for healthiness of boiler. Due to single ash drain line in each bed of furnace, It is inadequate to drain out the clinker completely  from the opposite side of furnace bed(existing drain line).

It was suggested by M/S Thermax to provide an extra bed ash drain line to drain out the clinker from both side of furnace for healthy boiler operation.

5 nos extra ash drain line provided (extra each drain line in each bed)

9.2 ECONOMISER

9.2.1 SS STRAY TUBE ARRANGEMENT PROVIDED AT ECONOMISER TOP ZONE

Problem

Ash erosion rate is very high in economizer, due to this high ash erosion the thickness of economizer coil getting low and cause of frequent economizer coil leakage and boiler shutdown.

It was suggested by M/S Thermax to provide single layers of schematic stray of SS pipes at the top zone of economizer for protecting the economizer coil from high ash erosion rate at this area. This tray will help to kill the ash velocity at economizer zone.

SS stray tube arrangement in economizer top zone

9.2.2 SS BOX ARRANGEMENT PROVIDED AT ECONOMISER L BENDS

Problem

Ash erosion rate is very high in economizer, due to this high ash erosion the thickness of economizer coil getting low AT U-bends and cause of frequent economizer U-bend leakage and boiler shutdown.

It was suggested by M/S Thermax to provide SS box arrangement at U-bend area(25th  to 47th no )of economizer coil at top zone of economizer for protecting the economizer U-bends from high ash erosion rate at this area.

SS box arrangement in Economiser U bends of top zone

9.2.3 ANTICHANNELING PLATE PROVIDED

Due to high ash erosion in economizer bend area,bends are eroded and leaked frequently. antichanneling plate of 80 mm wide, provided at 6 places in economizer To avoid leakages and protecting from ash erosion

9.3 SPRING SUPPORT PROVIDED AT ATTEMPERATOR HEADER

Problem

Primary sup.heater O/L header(Attemprator header) & Inbed sup.heater I/L header dislocated from its original position due to dislocation of existing trunion support in attemperator header.

M/S Thermax suggested to provide two nos of spring support instead of existing trunion support in Attemperator header for avoiding above said problem.

Dislocated condition of attemperator header           hanging Spring support(1st) provided at attemperator header

Spring support(2nd) provided at attemperator header

10. MISC JOBS

10.1 DCF MAINTENANCE

There are 5 nos of drag chain coal feeder in Boiler-2.

Activity involved

1. Damaged bearing replaced

2. Damaged shaft replaced

3. Damaged sprocket replaced

10.2 REPLACEMENT OF COAL NOZZLE ASSEMBLY

Complete 30 nos of coal nozzle assembly have been replaced in Furnace.

10.3 ESP MAINTENANCE

Activity involved

1.Damaged collecting hammer replaced

2.Damaged shock bar replaced(collecting zone)

3.Damaged emitting hammer replaced

4.Damaged shock bar replaced(emitting zone)

Collecting zone maintenance work is under progress

10.4 FAN MAINTENANCE

FD FAN MAINTENANCE

Both side bearing replaced in FD fan-2A & 2B alignment done on dated 06.04.14 and readings are given below.

FD fan 2A

Radial			               Axial1			              Axial2

(0.0)                                      (0.00)                                         (-0.08)

(+0.01)----R-----(+0.02)       (+0.01) -----A1----- (-0.01)            (-0.03) -----A2------ (0.01)

(+0.03)                                  (-0.05)                                            (0.0)

FD fan 2B

Radial			               Axial1			              Axial2

(0.0)                                      (0.00)                                         (+0.03)

(-0.02)----R-----(-0.04)       (+0.02)   ---- A1----- (+0.02)            (+0.03) -----A2------ (0.0)

(-0.05)                                     (+0.04)                                            (0.0)

ID FAN MAINTENANCE

Both side bearing replaced in ID fan-2A & 2B alignment done on dated 11.04.14 and readings are given below.

ID fan 2A

Radial			               Axial1			              Axial2

(0.0)                                      (+0.01)                                         (+0.03)

(+0.01)----R-----(+0.0)          (+0.05) -----A1----- (0.0)                  (0.0) -----A2------ (+0.02)

(+0.02)                                  (+0.05)                                          (-0.02)

ID fan 2B

Radial			               Axial1			              Axial2

(+0.02)                                      (+0.06)                                         (+0.04)

(+0.01)----R-----(-0.0)        (+0.1)   ---- A1----- (+0.0)               (+0.01) -----A2------ (0.0)

(-0.03)                                     (+0.03)                                            (-0.03)

PA FAN MAINTENANCE

Both side bearing replaced in PA fan-2A & 2B alignment done on dated 30.04.14 and readings are given below.

PA fan 2A

Radial			                  Axial

(+0.02)                                      (5.68)

(+0.0)----R-----(+0.01)           (5.70) -----A----- (5.68)

(+0.01)                                  (5.70)

PA fan 2B

Radial		                 Axial

(+0.02)                                      (5.57)

(+0.0)----R-----(+0.03)             (5.60) -----A----- (5.57)

(-0.01)                                       (5.60)

10.5 DAMPER REPLACEMENT/MAINTENANCE

Activity involved

1.5 nos of wind box damper replaced-these dampers were in damaged condition and continuous air passing through wind box damper and it create lit-up difficulity and operation unhealthiness,due to this above said problem management decided to replace complete 5 nos of wind box dampers.

Maintenance of Other various dampers

| Sl.No. | Discreption of dampers | Problem | Maintenance |
| --- | --- | --- | --- |
| 1 | ID fan 2A suction damper | It was jammed and some passing at the time of operation | Maintenace done for damper freeness |
| 2 | ID fan 2A IGV | It was jammed and some passing at the time of operation | Oiling done in bush bearing, maintenance done |
| 3 | ID 2A discharge damper | It was jammed | Maintenance done and damper made free |
| 4 | ID fan 2B suction damper | 2 links were in lock condition, passing at the time of operation | 2 links cutting done and refitted with new rectified lever |
| 5 | ID fan 2B IGV | Lightly jammed and passing | Maintenance done and damper made free |
| 6 | ID 2B discharge damper | It was jammed | Maintenance done and damper made free |
| 7 | OFA damper | Both dampers were jammed | Maintenance done and damper made free |
| 8 | FD fan 2A discharge damper | Lightly jammed | Maintenance done and damper made free |
| 9 | FD fan 2B discharge damper | Lightly jammed | Maintenance done and damper made free |
| 10 | PA fan 2A suction damper | Damper hinge lock to be adjusted | Locking arrangement rectified |
| 11 | PA fan 2A discharge damper | Jammed and damper cover was open | Spindle and square block replaced and damper made free |
| 12 | PA fan 2B suction damper | OK | Checked and found ok |
| 13 | PA fan 2B discharge damper | Jammed and damper cover was open | Spindle and square block replaced and damper made free |

ID fan damper maintenance

Wind box damper maintenance

10.6 APH TUBE MAINTENANCE

RFTE done at APH tube and found some of the tubes are low thickness and leaked condition. Physical inspection also done and as per physical inspection few more tubes are found corroded.

SS ferrule fitting done at damaged tubes,100 nos of ferrule fitted in damaged tubes.

RFET at APH tube                                                   SS ferrule fitted at damaged APH tubes

10.7 PA LINE MAINTENANCE

Problem

PA lines thickness was low and patch welded at many lines,Due to these leakages PA pr.was not sufficient for coal conveying and cause of PA line chocking as well as It creates heavy coal leakage through PA lines and cause of environmental pollution.5 nos of cross piece were also in damaged condition.

Management decided to replace all 30 nos of PA lines of SS 304 to avoid coal leakage and smooth coal conveying through PA lines. Damaged 5 nos of cross piece also replaced.

30 nos of PA line replaced

10.8 FURNCE CLEANING, PINNING & BED MATERIAL CHARGING

Boiler furnace is basically divided in 05 beds. One bed contains approx. 13 sets. of in bed evaporator coils, 5 Nos coal nozzles & 1100 air nozzles. There are 16/9 holes in each air nozzles.It is very difficult to do above said process due to congested  area under evaporator coil in furnace.

Activity involved

- Furnace cleaning

- Air nozzle exposing

- Bubble caps pinning

- Bed material charging for fluidization.

- Bed material charging in 1st bed for boiler lit-up for refractory dryout & Alkali boilout.

- Bed material charging in 1st bed for boiler lit-up for Steam blowing

- Clinker removal (which was made in steam blowing)from three bed and bed material charging for Final boiler lit-up.

Bubble caps Pinning work is under progress in furnace

10.9 PAINTING JOBS DURING SHUTDOWN

HR painting done at various places in boiler-2 during shutdown.

Downcomers(before painting)                                   Downcomers(after painting)

Risers tubes(before painting)                                   Risers tubes(after painting)

Steam drum (before painting)                                               Steam drum(after painting)

10.10 DIESEL BURNER REPLACEMENT

Problem

Diesel burner found damaged and due to this, flame length got disturbed at the time of strat-up diesel firing

Management decided to replace Inner diesel burner assembly to avoid this above said difficulty.

Diesel burner -2 replaced in furnace

10.11 VALVE REPLACEMENT

Various valve replaced during shutdown, these valve were passing and damaged condition. Details of replaced valves are given below.

1. Attemperator control valve

2. Panel ring header drain valve

3. Economiser bottom header drain valve.

4. Economiser top header drain valve.

Attemperator control valve replaced                        Drain vale replacement

10.12 FLOW METER ARRANGEMENT AT CBD LINE

Flow meter is required in CBD line to know the exact quantity of blow down through CBD.

Orifice fitted and welded in 1” CBD line for flow meter.

10.13 HYDROTEST

After completion of pr.parts replacement,hydrotest done at 1.5 times of maximum working pressure of boiler i.e. 112.5 Kg/cm2.Few leakages found and same are attended and hydro test successfully completed at required mentioned pressure.

11 COMMISSIONING OF BOILER

In the commissioning of boiler several activities involved,list of activities are given below

11.1 Refractory dryout & alkali boil out.

11.2 Steam blowing

11.1 REFRACTORY DRY OUT AND ALKALI BOIL OUT

OBJECTIVE

The objective of this procedure is to ensure proper drying, curing of refractory applied in the combustor and other component.The castable usually undergo considerable chemical changes during initial heating through these reactions snsures maximum strength.

Purpose of alkali boil out is to remove deposits like oil,greese,mill scale etc.Resulting out of manufacturing.fabrication and erection procedure from boiler internals.Such deposits in the boiler tubes walls restrict heat transfer across the tube wall resulting failure due to overheating.

Quantity  of chemicals (considering water holding capacity of boiler)

Hydrous Tri-sodium Phosphate(Na3PO4.12H2O)=4600ppm, Anhydrous Di –sodium Phosphate(Na2HPO4)=1000 ppm, Wetting agent(surfactant/Detergent) =225  ppm

Pre-Requisites

1.Ensure the following pre-commissioning checks for the refractory dryout.

2.Ensure the avalibility of adequate feed water as per recommendation,adequate bed materials,adequate oil quantity for oil firing,draft system and instruments required for boiler firing.

3.Make sure that test gags are removed from safety valves

4.Fill the compartment with refractory bed material 300 mm above the bubble caps.

6.Ensure the avalibility of adequate qualified boiler operating staff.

7.Readiness of sample collection system.

8.Water testing facilities including pH and oil testing detection.

9.Readiness of chemical dosing system

10. Confirm the blow down and drain connections are terminated to safe location.

11.Fill the drum with the specified quantity feed water 200 mm below the manhole opening .Exact quantity of chemicals is to be carried in dry form to the drum level platform. Chemicals are to be dissolved in DM water externally in a container near the drum manhole in batches. The concentrated solutions so prepared are to be poured into the drum through the manhole. Or thru top nozzle when the entire quantity of chemical has been charged into the drum, close the manhole/nozzle with proper sill and hardware.

Procedures

1.Start the fan and adjust the air flow at minimum airflow required for burner light up.

2.Before taking the trial,gas should be vented in to atmosphere through header vent to remove the nitrogen or any incombustible gases present in the piping.

3.Before going for burner light up all the pre-interlock,purge interlocks,purging and main interlocks need to be satisfied.

4.After satisfying the above condition burner is ready for start.

5.Adjust the oil control valve at minimum position to avoid heavy ingress of fuel in the boiler.

6.With burner start command spark will be generated in the gas lighter gun and fuel SOV will open.

7.With the help of pilot flame the main fuel (oil) will will ignite.

With the above procedure the burner flame will be established.

8.For proper checking and setting of the flame the burner can be keep in running condition till all trials are complete.

9.Increase the firing rate in such a way that the raise in flue gas temperature at Economiser I/l  at approx.25 deg./hr.Whenever the temperature reaches 100 deg .Hold temp. for 5 hrs at 100 deg C for removing moisture from refractory castable.If the temp. falls,increase the firing rate and maintain the required temp.

10.After refractory soaking ,raise the temp of flue gas at economizer I/L again @ 25 deg c/hr to 125 deg c and hold the temp for 5 hrs for setting of refractory castable.

11.Raise boiler pressure as per cold start up pressure rising curve.

12.Boil-out pressure and duration

Rise the boiler pressure to 50 % of working pressure(drum) or 40kg/cm2 whichever is lower .Carry out the boil-out operation  by maintaining this pressure for a period of 12 hours. Pressure is to be maintained by controlling the fuel firing and modulation of the start up vent.

13.Blowdown

On attaining approx. 5 kg/cm2 drum pressure, quickly operate the intermittent blow down for 10 sec. Restore drum level to N.W.L. Allow drum pressure to raise upto a value which is 50% of operating pressure or 40kg/cm2 whichever is lower. Leave the CBD valve slightly open to prevent choking of sample line and sample cooler. Operate the IBD for 10 sec once every hour. Ensure that water level in drum is replenished each time. At the time of 12 hours of boil-out operation., sample of boiler water is tested for oil traces to determine the end point of the process. If the oil levels are not reducing to the desired limit, even after adequate draining, chemicals may be added to the drum through HP dosing system

14. Completion of Boil-out

Boiler water sample is analyzed for presence of oil. When analysis confirms that oil present in the sample is within limits (=/<5 ppm) the boilout operations treated as complete. Fur confirmation it is adviced to collect 3 samples within 5 minutes span at the end of boilout operations and check the consistency of results

15.Post Boilout operations

Box up the boiler and allow the until feedwater pH is in close proximity with drain sample’s pH. When the drum pressure drops to atmospheric, start draining the boiler slowly and in mean time make up the level with feed water. Stop rinsing when the drain water sample pH is in close proximity with the inlet feedwater  pH. After rinsing drain the boiler completely, cut the inspection caps of all the bottom headers for inspection and cleaning of sediments if any. In case of in-bed evaporator tubes, both inbed coils bottom and top header end caps and inspection caps needs to be cut and inspected. It is to be cut and inspected. It is to be ensured that all the drain holes in the baffle plates to be clean and free from any blockage from foreign materials like weld slag/welding consumables . Open the steam drum manholes and re,ove the sediments (if any). Backflushing of super heaters and flushing of the downcomers, supply pipes convection tubes thoroughly. Re-weld the end caps on headers as per the recommended procedures. After welding, radiography and post weld heat treatment of the weld joints (if req.)to be carried out prior to hydro test of the boiler.

11.2  STEAM BLOWING

Objective

Steam blowing is carried out for removing foreign particles like rust, dirt scale, and welding burr from the boiler system to prevent any impact to steam driven equipment .

Pre-requisites

1.Before proceeding with steam blowing the following activities need to be completed.

2.Completion of temporary exhaust piping including reaction supports

3 .Removal of internals of  NRV and FLOW NOZZLE on main steam line.

4.Operatibility of boiler stop valve.

5.Readiness of boiler for operation.

6.Readiness of start up vent valve for operation.

7.Readiness of instrumentation namely drum level transmitter, pressure indicators, pressure transmitters, direct level guage and necessary instrumentation for safe boiler operation.

8.Readiness of feed water system and feed water pump.

9.Availibility of qualified boiler operators and operating staff.

10.Adequate safety equipments and first aid kit for operating personnel for protection against high noise level and hot surfaces

11.Equipment’s start up in sequence along with all safety protections for all the equipment.

12.Do not insulate steam piping

13.Load spring supports.

14.Ensure piping support are properly done as per drawing.

15.All the boiler safety interlocks like drum level very low, furnace pressure high, steam temperature high, equipment’s trip interlocks etc.

16.Control valves readiness for boiler level, deaerator level etc.

17.Motorized valves

18.Temperature gauges and transmitters.

19.Draft gauges and transmitters.

20.Controllers and others panel instruments. Annunciators

Preparation

1.The safe location for releasing the steam will be decided at site preferably from the flange joint nearer to battery limit or at the process end of the piping. Temporary exhaust pipe shall be such that it is after the manual isolation valve on line and adequate structural components like beams, etc. are available for locking against reaction forces.

2.To check the extent of removal of foreign particles, target plates are installed near the inlet of the temporary exhaust pipe. Target plates are rectangular plates of soft material like aluminium etc. which would get impingement by articles blowing off with steam.The target plates are mirror finish on one face and fitted on rigid M.S. mounting with the machined face, facing the blowing steam.

3.When the impingement noticed on target plates are within acceptable limits, steam blowing is declared as complete.

Procedure

1.Fill the boiler with specified quantity feed water to NWL. Light up the boiler as per cold start up procedure .

2.Rise the boiler pressure gradually to 50 % of working pressure or 40 kg/cm2 whichever is lower by controlling fuel firing/modulating the start up vent as required.

3.Ensure all the pre-requisites are completed.

4.Ensure the operation of the MSSV in remote mode and keep the valve in closed condition.

5.Initially the steam blowing cycle is done at lower pressure @20kg/cm2to flush pipeline, to remove the foreign particle which may damage the line valve component and also to study the pip[e support, thermal expansion etc.

6.Before blowing ensure there is no condensation in the line & dry steam is coming out through All the drains  and from the main steam piping. Raise main steam temperature to operating parameter.

7.Drop the steam drum level to 35%.

8.After warming up the steam line throttle the start-up vent valve and simultaneously open the MSSV. Close the MSSV  when steam drum pressure drops to 10 kg/cm2.Repeat the blowing @ 20kg/cm2 for 3-4 times.

9.Whenever the MSSV is opened the steam drum level will shoot up which happens due to swelling. Restrict drum level within 70% by adjusting the MSSV opening. Hence allow feed water gradually to make up steam relieved and closely watch the drum level in the field as well as in DCS during blowing. Also monitor the main steam temperature. This should not drop < 1000C while blowing.

10.Check the condition of main steam piping supports after initial blows and ensure no abnormalities support system. Repeat the exercise and confirm integrity.

11.After ensuring pipe support increase blowing pressure to 40 kg/cm2 or 50 % of the working pressure whichever is lower. Follow the procedure of blowing, drop the drum pressure to 20 kg/cm2, clo9se MSSV. Maintain drum level at 50 %.

12.Leave sufficient interval(approx 2 hours ) in between steam blowing cycle so that the main steam piping cools down i.e., pipe skin temperature should drop at least by 1000C

13.Repeat the above steam blowing exercise several times as along as you could visibly observe as the steam blowing is clear

14.Now, isolate MSSV and insert soft metal target plate in the target plate holder provided for temporary piping. Raise steam drum pressure to 40 kg/cm2. Repeat the blowing one time with the target plate. Close main steam valve and remove target plate. If the target plate is not clean, repeat steam-blowing cycle for 4 to 5 times without target plate can be inserted and checked.

15.Target plate will be checked as per the acceptance criteria and upon acceptance, the steam blowing is said to be completed.

16. Remove temporary piping and supports provided for steam provided for steam blowing. Reinstate the main steam piping.

17. Now the flow nozzle can be installed. Insulation of piping can be done

Commissioning engineer from M/S Thermax  ,Mr.D.Mukherjee was deputed to look after commissioning activities.All activities have been performed as per Commissioning procedure ,which was given by M/S Thermax & according to the guidelines of commissioning engineer.

BOILER LIT-UP AND STEAM CHARGING

Boiler lit-up as per cold start-up procedure and steam charged on dated  20.06.2014,03.20 AM.

13. ANNEXURES

13.1 ACTUAL SHUTDOWN COSTING

| BOILER-2 SHUTDOWN COSTING |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sr. NO. | MATERIAL DESCRIPTION | P.O. NO. | VENDOR NAME | P.O. VALUE(Rs.) | P.O QUANTITY | CONSUMED QTY DURING SHUTDOWN | ACTUAL SHUTDOWN COST |
| 1 | Supervision for Boiler banktube | 252004140355 | M/S:Thermax Ltd | 873000.00 | 45 man days | 45 man days | 873000 |
| 2 | phoscast refractory | 252004140661 | M/S:Thermax Ltd | 960000.00 | 2.00 | 1.00 | 480000 |
| 3 | Application of Phoscast Refractory in AFBC Boiler ( OR - 805 & OR - 806) as per annexure enclosed. | 252004140683, | M/S:Thermax Ltd | 577600.00 | 2.00 | 1.00 | 288800 |
| 4 | Coal nozzle assembly for AFBC Boiler. | 252004141600 | M/S:Thermax Ltd(Mr.Vasu) | 799800.00 | 30 nos | 30 nos | 799800 |
| 5 | Supply of Inbed evaporator coil | 252004141592 | M/S:Thermax Ltd(Mr.Vasu) | 2520144.00 | 264 nos | 264 nos | 2520144 |
| 6 | SS 304 , Ferrules for air pre - heater tubes. | 252004141703 | M/S:Thermax Ltd(Mr.Vasu) | 380000.00 | 1000 | 100 | 38000 |
| 7 | Level gauge | 252004140286 | Levcon instruments pvt ltd | 2,00,270.00 | 2 nos | 2 nos | 200270 |
| 8 | Diesel burner LU-325 | 252004140975 | Wesman thermal engg pvt ltd | 3,50,479.00 | 1 no | 1 no | 350479 |
| 9 | Insulation castable for AFBC Boiler. | 252004141578 | M/S Mahakoshal Refractory. Mob. - 09301850093, Mr. Pathak | 600000.00 | 25 tonn | 16 tonn | 384000 |
| 10 | Contract for replacement of economiser coil & convection bank tubes | 252004141801 | M/S Unique Constructions Engg. | 4629814.00 | Complete replacement of economiser coil & convection bank tubes | Completed | 4629814 |
| 11 | Asbestos rope for economiser casing | 252004141483 , | M/S J.D. Jones & Co. , Mob. No. - 09631087989 , 9631010243(e MAIL: comments@jdjones.com) | 10972.00 |  |  | 10972 |
| 12 | Shield of Economiser straight tube | 252004141835 | M/S:Techno Engg. Rubber Industries, Kolkata | 350000.00 | 2500 nos | 2500 nos | 350000 |
| 13 | ESP Spares, Type - FPA - 3 X 52.5 M-64 -90-A-2 | 252004141755 | M/S Alstom India Ltd. | 367567.35 | various spares of ESP | Inner arm,outer arm and shock anvil replaced | 100000 |
| 14 | Contract for IBR Jobs in Power Plant. | 252004141837 | M/S Royal Enterprises. | 3753700.00 | Various IBR jobs in AFBC Boiler | Bed coil,IBSH coil,valve replacement | 1669400 |
| 15 | Contract for Scaffolding work | 252004142305 | M/S Unique Constructions Engg. |  | Scaffolding jobs in various places | Scaffolding jobs in various places | 253226 |
| 16 | Support for Inbed Superheater coil. | 252004142200 | M/S:Thermax Ltd | 2470000.00 | 2 nos | 1 no | 1235000 |
| 17 | Economiser coil for AFBC boiler | 252004140478 | M/S:Thermax Ltd | 5189500.00 | Complete set | Complete set | 5189500 |
| 18 | Convection bank tube supply, | 252004140354 | M/S:Thermax Ltd | 3390006.60 | Complete set | Complete set | 3390006.6 |
| 20 | 5" Dia. SS - 304 pipe and C.S Flanges for Boiler. | 252004141274 | Metal Industrial Corporation, Ph - 022 - 23894633 | 1284900.00 | Complete replacement of PA line | Completed | 1284900 |
| 21 | Spares for various safety valves | 252004140923 | Manjil Enterprises | 1896398.00 | Svarious spares of different types of valves | Used as per requirement | 400000 |
| 22 | wire mesh | 252004141589 | M/S Max Steel | 245223.00 | 100 tonn | 100 tonn | 245223 |
| 23 | Mud drum repair job | 252004150275 | M/S Royal Enterprises. | 440000.00 | Mud drum repairing | completed | 440000 |
| 24 | Contract for Misc.Maintenance job | 252004141696 | M/S Jai maa tarini | 2518200.00 | Various maintenance activities | Used as per requirement | 476000 |
| 25 | Spring support for attemperator header | 252004150235 | M/S Thermax Ltd. | 162000.00 | 2 set | 1 set | 81000 |
| 26 | Contract for ash drain line and PA line replacement,windbox damper maintenance | 252004142443 | M/S Shakti engineering ltd. | 879581.00 | Fabrication and erection jobs | Completed as per requirement | 879581 |
| 27 | Contract for ESP repair | 252004131662 | M/S Indo constructions | 534662.00 | Various ESP repairing & maint.jobs | Completed as per requirement | 100000 |
| 28 | Clinker removal and furnace cleaning | 252004140161 | M/S Balbhadra enterprises | 743600.00 | 100.00 | 10 | 74360 |
| 29 | Hot insulation job in AFBC Boier | 252004140625 | M/S Kalinga insulations | 6598332.00 | Various hot insulation jobs in AFBC Boiler(corrugated sheets) | As per requirement | 1000000 |
| 30 | Refractory removal and application of refractory | 252004140834 | M/S Western corrosion controller | 735000.00 | 600 m2 | 200 m2 | 230000 |
| 31 | Pr.parts cleaning in AFBC Boiler | 252004142305 | M/S Unique Constructions Engg. | 550000.00 | 2 nos | 1 no | 275000 |
| 32 | IBR jobs in powerplant | 252004131665 | M/S Unique Constructions Engg. | 4135000.00 | Various IBR jobs in power plant | As per requirement | 1328210 |
| 33 | CPR for Die sodium phosphate | 252004142399 | M/S AVM sales coorporation | 9500.00 | 100 Kg | 80 Kg | 7600 |
| 34 | CPR for detergent | 252004150072 | IFFCO Paradeep employee consumer cooperative society | 3540.00 | 20 | 18 | 3186 |
| 35 | Tri sodium phosphate | 252004140305 | M/S AVM sales coorporation | 856000(it is regular consuming item for Boiler &SAP both) | 8000 Kg | 368 | 39376 |
| 36 | Hot insulation of furnace wall in AFBC Boiler | 252004141334 | M/S Kalinga insulations | 712400.00 | 520 m2 | 200 | 274000 |
| 37 | Expansion bellows for furnace ash drain line. | 252004142371 | M/Thermax Ltd. | 159400.00 | 10 nos | 5 nos | 79700 |
| 38 | Commissioning engineer for Commissioning activities in AFBC Boiler | 252004150414 | M/Thermax Ltd. | 155200.00 | Various commissioning activities in AFBC Boiler | 1 | 155200 |
| TOTAL SHUTDOWN COST |  |  |  |  |  |  | 30135748 |

| 13.2 TIME CHART OF BOILER-2 SHUTDOWN ACTIVITIES |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.L | Job Description | Duration(days) | Start(Day) | Finish(Day) |
|  | Boiler shutdown to Boiler start up | 80 | 1st April | 20th June |
|  | Boiler stoppage | 31.03.14,10.30 PM |  |  |
| 1 | Furnace Cooling | 1 | 1st April | 1st April |
| 2 | Scaffolding in furnace and IBR cleaning | 4 | 2nd April | 5th April |
| 3 | Critical jobs | 57 | 6th April | 27th May |
| 3.1 | Convection bank tube replacement(740 nos of tube replacement between steamdrum & muddrum) | 57 | 6th April | 27th May |
| 3.2 | Economiser job | 48 | 3rd April | 22nd May |
| 3.2.1 | Casing removal of economiser | 3 | 3rd April | 5th April |
| 3.2.2 | complete Economiser coil replacement | 34 | 6th April | 10th May |
| 3.2.3 | Economiser casing erection & misc fabrication | 11 | 11th May | 22nd May |
| 3.3 | Complete Evaporator bed coil replacement with fixing of Phoscast-90 refractory&rplacement of Y piece at furnace wall.(264 nos coil replacement) | 45 | 6th April | 20th May |
| 3.4 | Inbed super heater replacement & support modification(24 nos coil replacement) | 42 | 6th April | 18th May |
| 3.5 | CA-RLA study | 35 | 6th April | 10th May |
| 3.6 | Various modifications for boiler healthiness | 35 | 15th April | 20th May |
| 4 | Hydrotest & required leakage attending | 6 | 27th May | 2nd June |
| 5 | Steam blowing arrangement and steam drum internal fitting | 4 | 3rd June | 6th June |
| 6 | Commissioning of Boiler | 8 | 7th June | 14th June |
| 7 | Clinker removal,Furnace cleaning and air nozzle pinning | 5 | 15th June | 19th June |
| 8 | Boiler lit-up and steam charging | 1 | 20th June,3.20 AM |  |